## Rules
Rule ID | Ruleset Reference | Rule Description | Applicable RMR | Rule Assertion | Comparison Value | Rule Dependency | Mandatory Rule | Data Table Reference | Notes
5-1 | [8 empty] | Hold off until we get confirmation from Supriya
5-2 | G3.1 #1 (a) The simulation model of the proposed design shall be consistent with the design documents… | Orientation is the same in user model and proposed model | Proposed RMR | = | User RMR | None |  | Reference to data tables in 90.1 | Multiple rule dependency can be separated by a comma
5-3 | G3.1 #5(a), baseline column: The building shall be modeled so that it does not shade itself. | Baseline building must be modeled so that it doesn't shade itself | Baseline RMR | = | Expected Value | None |  | Reference to data tables in 90.1 | Multiple rule dependency can be separated by a comma
5-4 | G3.1 #5 (b) Opaque assemblies used for new buildings, existing buildings, or additions shall conform with assemblies detailed in Normative Appendix A | Baseline roof assemblies must conform with assemblies detailed in Appendix A | Baseline RMR | = | Expected Value | None |  | Reference to data tables in 90.1 | Multiple rule dependency can be separated by a comma
5-5 | G3.1 #5 (b) Opaque assemblies used for new buildings, existing buildings, or additions ... shall match the appropriate assembly maximum U-factors in Tables G3.4-1 through G3.4-8: | Baseline roof assemblies must match the appropriate assembly maximum U-factors in Tables G3.4-1 through G3.4-8 | Baseline RMR | = | Expected Value | None |  | Reference to data tables in 90.1 | Multiple rule dependency can be separated by a comma
5-6 | G3.1 #1 (a) The simulation model of the proposed design shall be consistent with the design documents… | Building enevelope U-factors must be modeled in proposed design as designed | Proposed RMR |  | User RMR | None |  | Reference to data tables in 90.1 | Multiple rule dependency can be separated by a comma
5-7 | G3.1 #5 (b) Opaque assemblies used for new buildings, existing buildings, or additions shall conform with assemblies detailed in Normative Appendix A | Baseline below-grade walls shall conform with assemblies detailed in Appendix A Concrete block, A4) | Baseline RMR | = | Expected Value | None |  | Reference to data tables in 90.1 | Multiple rule dependency can be separated by a comma
5-8 | G3.1 #5 (b) Opaque assemblies used for new buildings, existing buildings, or additions ... shall match the appropriate assembly maximum U-factors in Tables G3.4-1 through G3.4-8: | Baseline below-grade walls shall match the appropriate assembly maximum C-factors in Tables G3.4-1 through G3.4-8 | Baseline RMR | = | Expected Value | None |  | Tables G3.4-1 to G3.4-8 | 1. Specified Test Scope as "project" because RDS's would need to account for conditioning categories of adjacent zones. However, the provided TCDs are for single-zone building, so tests are actually at per-surface basis.
5-9 | G3.1 #1 (a) The simulation model of the proposed design shall be consistent with the design documents… | Below-grade wall C-factor must be the same in the proposed model as in the user model | Proposed RMR | = | User RMR | None |  | No | U-RMR = P-RMR verification
5-10 | G3.1 #5 (b) Opaque assemblies used for new buildings, existing buildings, or additions shall conform with assemblies detailed in Normative Appendix A | Baseline above-grade wall assemblies must conform with assemblies detailed in Appendix A (Steel-framed A3.3) | Baseline RMR | = | Expected Value | None |  | No | Properties of individual materials not provided, only constructions an be verified
5-11 | G3.1 #5 (b) Opaque assemblies used for new buildings, existing buildings, or additions ... shall match the appropriate assembly maximum U-factors in Tables G3.4-1 through G3.4-8: | Baseline above-grade wall assemblies must match the appropriate assembly maximum U-factors in Tables G3.4-1 through G3.4-8 | Baseline RMR | = | Expected Value | Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories |  | Tables G3.4-1 to G3.4-8
5-12 | G3.1 #5 (b) Opaque assemblies used for new buildings, existing buildings, or additions shall conform with assemblies detailed in Normative Appendix A | Baseline floor assemblies must conform with assemblies detailed in Appendix A (Floors—Steel-joist (A5.3)) | Baseline RMR | = | Expected Value | None |  | No
5-13 | G3.1 #5 (b) Opaque assemblies used for new buildings, existing buildings, or additions ... shall match the appropriate assembly maximum U-factors in Tables G3.4-1 through G3.4-8: | Baseline floor assemblies must match the appropriate assembly maximum U-factors in Tables G3.4-1 through G3.4-9 | Baseline RMR | = | Expected Value | Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories |  | Yes, Tables G3.4-1 to G3.4-8
5-14 | G3.1 #5 (b) Opaque assemblies used for new buildings, existing buildings, or additions shall conform with assemblies detailed in Normative Appendix A | Baseline slab-on-grade assemblies must conform with assemblies detailed in Appendix A ( unheated slabs from tables (A6).) | Baseline RMR | = | Expected Value | None |  | No
5-15 | G3.1 #5 (b) Opaque assemblies used for new buildings, existing buildings, or additions ... shall match the appropriate assembly maximum U-factors in Tables G3.4-1 through G3.4-8: | Baseline slab-on-grade assemblies must match the appropriate assembly maximum F-factors in Tables G3.4-1 through G3.4-9 | Baseline RMR | = | Expected Value | Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories |  | Yes, Tables G3.4-1 to G3.4-8
5-16 | G3.1 #1 (a) The simulation model of the proposed design shall be consistent with the design documents… | Slab-on-grade F-factor in the proposed design must be modeled as-designed | Proposed RMR | = | User RMR | None |  | No
5-17 | Table G3.1 #1, Baseline column: The baseline building design shall be developed by modifying the proposed design as described in Section G3. Except as specifically instructed, all building systems and equipment shall be modeled identically in the proposed design and baseline building design. | Opaque surfaces that are not regulated (not part of opaque building envelope) must be modeled the same U/C/F-factor in the baseline as in the proposed design | Baseline RMR | = | Proposed RMR | None |  | No
5-18 | Table G3.1 #5 baseline column #c: For building area types included in Table G3.1.1-1, vertical fenestration areas for new buildings and additions shall equal that in Table G3.1.1-1 based on the area of gross above-grade walls that separate conditioned spaces and semiheated spaces from the exterior. | For building area types included in Table G3.1.1-1, vertical fenestration areas for new buildings and additions shall equal that in Table G3.1.1-1 based on the area of gross above-grade walls that separate conditioned spaces and semiheated spaces from the exterior. | Baseline RMR | = | Expected Value | None |  | Yes,Table G3.1.1-1
5-19 | Table G3.1 #5 baseline column #c: For building areas not shown in Table G3.1.1-1, vertical fenestration areas for new buildings and additions shall equal that in the proposed design or 40% of gross above-grade wall area, whichever is smaller | For building areas not shown in Table G3.1.1-1, vertical fenestration areas for new buildings and additions shall equal that in the proposed design or 40% of gross above-grade wall area, whichever is smaller, | Baseline RMR | = | Expected Value | None |  | Yes,Table G3.1.1-1
5-20 | Table G3.1 #5 baseline column #c: Where a building has multiple building area types, each type shall use the values in the table. | Where a building has multiple building area types, each type shall use the values in the table. | Baseline RMR | = | Expected Value | None |  | No
5-21 | Table G3.1 #5 baseline column #c: The vertical fenestration shall be distributed on each face of the building in the same proportion as in the proposed design. | The vertical fenestration shall be distributed on each face of the building in the same proportion as in the proposed design | Baseline RMR | = | Expected Value | None |  | No
5-22 | Table G3.1 #5 baseline column #c: The fenestration area for an existing building shall equal the existing fenestration area prior to the proposed work and shall be distributed on each face of the building in the same proportions as the existing building. | The baseline fenestration area for an existing building shall equal the existing fenestration area prior to the proposed work | Baseline RMR | = | Expected Value | None |  | No
5-23 | G3.1 #1 (a) The simulation model of the proposed design shall be consistent with the design documents… | Fenestration area in the proposed design must be as-designed | Proposed RMR | = | User RMR | None |  | No
5-24 | Table G3.1 #5Baseline column #d: Vertical Fenestration Assemblies. Fenestration for new buildings, existing buildings, and additions shall comply with the following: • Fenestration U-factors shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 for the applicable glazing percentage for Uall. | Vertical fenestration U-factors for residential, non-residential and semiheated spaces in the baseline model must match the appropriate requirements in Table G3.4-1 through G3.4-8 for the appropriate WWR in the baseline RMR. | Baseline RMR | = | Expected Value | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline fenestration area is established correctly (Rules 18, 19, 20) |  | Yes, Tables G3.4-1 to G3.4-8
5-25 | G3.1 #1 (a) The simulation model of the proposed design shall be consistent with the design documents… | Fenestration (window and skylight) U-factors in the proposed model must match the user model | Proposed RMR | = | Expected Value | None |  | No
5-26 | Table G3.1 #5 Baseline column #d: Vertical Fenestration Assemblies. Fenestration for new buildings, existing buildings, and additions shall comply with the following: • Fenestration SHGCs shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value for SHGCall for the applicable vertical glazing percentage. | Vertical fenestration SHGC shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 | Baseline RMR | = | Expected Value | None |  | No
5-27 | G3.1 #1 (a) The simulation model of the proposed design shall be consistent with the design documents… | Fenestration (window and skylight) SHGC in the proposed model must match the user model | Proposed RMR | = | User RMR | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline fenestration area is established correctly (Rules 18, 19, 20) |  | Yes, Tables G3.4-1 to G3.4-8
5-28 | Table G3.1 #1, Baseline column: The baseline building design shall be developed by modifying the proposed design as described in Section G3. Except as specifically instructed, all building systems and equipment shall be modeled identically in the proposed design and baseline building design. | Fenestration that is not regulated (not part of building envelope) must be modeled with the same area, U-factor and SHGC in the baseline as in the proposed design | Baseline RMR | = | User RMR | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories |  | No
5-29 | Table G3.1 #5 baselne column (d) All vertical fenestration shall be assumed to be flush with the exterior wall, and no shading projections shall be modeled. | Baseline fenestration shall be assumed to be flush with the exterior wall, and no shading projections shall be modeled. | Baseline RMR | = | Baseline RMR | None |  | No
5-30 | G3.1 #1 (a) The simulation model of the proposed design shall be consistent with the design documents… | Proposed fenestration has the same shading projections as the user model. | Proposed RMR | = | User RMR | None |  | No
5-31 | Table G3.1 #5 Proposed column a.4: Manual fenestration shading devices, such as blinds or shades, shall be modeled or not modeled the same as in the baseline building design. Table G3.1#5 baseline column (d) Manual window shading devices such as blinds or shades are not required to be modeled. | Manual fenestration shading devices, such as blinds or shades, shall be modeled or not modeled the same as in the baseline building design. | Baseline RMR | = | Proposed RMR | None |  | No
5-32
5-33 | Table G3.1#5 a 4: Automatically controlled fenestration shades or blinds shall be modeled. | Automatically controlled fenestration shading devices must be modeled in the proposed design the same as in user model. | Proposed RMR | = | User RMR | None |  | No
5-34 | Table G3.1#5 baselnid column e. e. Skylights and Glazed Smoke Vents. Skylight area shall be equal to that in the proposed design or 3%, whichever is smaller. | If skylight area in the proposed desing is 3% or less of the roof surface, the skylight area shall be equal to that in the proposed design. | Baseline RMR | = | Expected Value | None |  | No
5-35 | Table G3.1#5 baselnid column e: If the skylight area of the proposed design is greater than 3%, baseline skylight area shall be decreased by an identical percentage in all roof components in which skylights are located to reach 3%. | If the skylight area of the proposed design is greater than 3%, baseline skylight area shall be decreased by an identical percentage in all roof components in which skylights are located to reach 3%. | Baseline RMR | = | Expected Value | None |  | No
5-36 | Table G3.1#5 baselnid column e: Skylight orientation and tilt shall be the same as in the proposed design. | Skylight area must be allocated to surfaces in the same proportion in the baseline as in the proposed design; Skylight orientation and tilt shall be the same as in the proposed design. | Baseline RMR | = | Expected Value | None |  | No
5-37 | Table G3.1#5 baseline column e: Skylight U-factor … shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Skylight U-factors for residential, non-residential and semiheated spaces in the baseline model must match the appropriate requirements in Table G3.4-1 through G3.4-8 | Baseline RMR | = | Expected Value | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline skylight area is established correctly (Rules 34,35) |  | Yes, Tables G3.4-1 to G3.4-8
5-38 | Table G3.1#5 baseline column e: Skylight… SHGC properties shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Skylight SHGC properties shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Baseline RMR | = | Expected Value | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline skylight area is established correctly (Rules 34,35) |  | Yes, Tables G3.4-1 to G3.4-8
5-39 | Table G3.1 #5 Proposed column a5: Automatically controlled dynamic glazing may be modeled. Manually controlled dynamic glazing shall use the average of the minimum and maximum SHGC and VT. | Automatically controlled dynamic glazing may be modeled. Manually controlled dynamic glazing shall use the average of the minimum and maximum SHGC and VT. | Proposed RMR | = | Expected Value | None |  | No
5-40 | Table G3.1 #5 baseline column: The exterior roof surfaces shall be modeled using ... a thermal emittance of 0.90. | The baseline roof surfaces shall be modeled using a thermal emittance of 0.9 | Baseline RMR | = | Expected Value | None |  | No
5-41 | G3.1 #1 (a) The simulation model of the proposed design shall be consistent with the design documents… Table G3.1 #5 Proposed column a3: The exterior roof surface shall be modeled using the aged solar reflectance and thermal emittance determined in accordance with Section 5.5.3.1.1(a). Where aged test data are unavailable, the roof surface may be modeled with a reflectance of 0.30 and a thermal emittance of 0.90. | The proposed roof surfaces shall be modeled using the same thermal emittance as in the user model if the aged test data are available, or equal to 0.9 default emmitance | Proposed RMR | = | User RMR | None |  | No | Show warning message if thermal emittalce differ from the default of 0.9. ("Where aged test data are unavailable, the roof surface may be modeled with a reflectance of 0.30 and a thermal emittance of 0.90."); Show message saying that P-RMR may not be equal to U-RMR if aged test data is not available.
5-42 | Table G3.1 #5 baseline column: The exterior roof surfaces shall be modeled using a solar reflectance of 0.30 | The baseline roof surfaces shall be modeled using a solar reflectance of 0.30. | Baseline RMR | = | User RMR | None |  | No
5-43 | G3.1 #1 (a) The simulation model of the proposed design shall be consistent with the design documents… Table G3.1 #5 Proposed column a3: The exterior roof surface shall be modeled using the aged solar reflectance and thermal emittance determined in accordance with Section 5.5.3.1.1(a). Where aged test data are unavailable, the roof surface may be modeled with a reflectance of 0.30 and a thermal emittance of 0.90. | The proposed roof surfaces shall be modeled using the same solar reflectance as in the user model if the aged test data are available, or equal to 0.7 default reflectance. | Proposed RMR | = | User RMR | None |  | No | Show warning message if solar reflectance differ from the default of 0.3. ("Where aged test data are unavailable, the roof surface may be modeled with a reflectance of 0.30 and a thermal emittance of 0.90."); Show message saying that P-RMR may not be equal to U-RMR if aged test data is not available.
5-44 | Table G3.1 #5 (b) proposed column: Infiltration shall be modeled using... adjustments for weather and building operation. These adjustments shall be made for each simulation time step and must account for but not be limited to weather conditions and HVAC system operation, including strategies that are intended to positively pressurize the building. | The infiltration modeling method in the baseline includes adjustment for weather and building operation. | Baseline RMR | = | Expected Value | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories |  | No
5-45 | Table G3.1 #1, Baseline column: The baseline building design shall be developed by modifying the proposed design as described in Section G3. Except as specifically instructed, all building systems and equipment shall be modeled identically in the proposed design and baseline building design. | The infiltration modeling method in the baseline includes adjustment for weather and building operation. | Proposed RMR | = | Proposed RMR |  |  | No
5-46 | Table G3.1 #5 (b) proposed column: Infiltration shall be modeled using the same methodology and adjustments for weather and building operation in both the proposed design and the baseline building design. | The Infiltration shall be modeled using the same methodology and adjustments for weather and building operation in both the proposed design and the baseline building design. | Proposed RMR | = | Proposed RMR |  |  | No
5-47 | Table G3.1 #5 baseline column (h): The air leakage rate of the building envelope (I75Pa) at a fixed building pressure differential of 0.3 in. of water shall be 1.0 cfm/ft2. | The baseline air leakage rate of the building envelope (I75Pa) at a fixed building pressure differential of 0.3 in. of water shall be 1 cfm/ft2. The air leakage rate of the building envelope shall be converted to appropriate units for the simulation program using one of the methods in Section G3.1.1.4. | Baseline RMR | = | Expected Value | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories |  | No
5-48 | Table G3.1 #1, Baseline column: The baseline building design shall be developed by modifying the proposed design as described in Section G3. Except as specifically instructed, all building systems and equipment shall be modeled identically in the proposed design and baseline building design. | The air leakage rate in unconditioned and unenclosed spaces must be the same in the baseline and proposed design | Baseline RMR | = | Proposed RMR | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories |  | No
5-49 | Table G3.1 #5 Proposed column (b): The proposed air leakage rate of the building envelope (I75Pa) at a fixed building pressure differential of 0.3 in. of water shall be 0.6 cfm/ft2 for buildings providing verification in accordance with Section 5.9.1.2. The air leakage rate of the building envelope shall be converted to appropriate units for the simulation program using one of the methods in Section G3.1.1.4. Exceptions: When whole-building air leakage testing, in accordance with Section 5.4.3.1.1, is specified during design and completed after construction, the proposed design air leakage rate of the building envelope shall be as measured. | The proposed air leakage rate of the building envelope (I75Pa) at a fixed building pressure differential of 0.3 in. of water shall be 0.6 cfm/ft2 for buildings providing verification in accordance with Section 5.9.1.2. The air leakage rate of the building envelope shall be converted to appropriate units for the simulation program using one of the methods in Section G3.1.1.4. Exceptions: When whole-building air leakage testing, in accordance with Section 5.4.3.1.1, is specified during design and completed after construction, the proposed design air leakage rate of the building envelope shall be as measured. | Proposed RMR | = | Expected Value | None |  | No
5-50 | Table G3.1 #14 baseline column: Same as proposed design. | Shading by adjacent structures and terrain is the same in the baseline and proposed. | Baseline RMR | = | Proposed RMR | None |  | No | a. If site shading is included in both the baseline and proposed, include a message to verify that it is the same in both.
5-51 | Table G3.1 #14 Proposed (a): a. Shading by Adjacent Structures and Terrain. The effect that structures and significant vegetation or topographical features have on the amount of solar radiation being received by a structure shall be adequately reflected in the computer analysis. All elements whose effective height is greater than their distance from a proposed building and whose width facing the proposed building is greater than one-third that of the proposed building shall be accounted for in the analysis. | Shading by adjacent structures and terrain is the same in the proposed design as in user model. | Proposed RMR | = | Proposed RMR | None |  | No
5-52 | Table G3.1 #14 Proposed (b): b. Ground Temperatures for Below-Grade Wall and Basement Floor Heat-Loss Calculations. It is acceptable to use either an annual average ground temperature or monthly average ground temperatures for calculation of heat loss through below-grade walls and basement floors. | It is acceptable to use either an annual average ground temperature or monthly average ground temperatures for calculation of heat loss through basement floors. | Baseline RMR | = | Proposed RMR | None |  | No
5-53 | Table G3.1 #5, Baseline Building Performance (b): Opaque door types shall be of the same type of construction as the proposed design and conform to the U-factor requirements from the same tables (A7). | U-factor of the baseline door is based on Tables G3.4-1 through G3.4-8 for the applicable door type (swinging or non-swinging) and envelope conditioning catoegory | Baseline RMR | = | User RMR | None |  | Yes, Tables G3.4-1 to G3.4-8
5-54 | Table G3.1 #5, Baseline Building Performance (b): Opaque door types shall be of the same type …. as the proposed design | subsurface.subclassification is the same in the B-RMR andn P-RMR | Baseline RMR | = | Proposed RMR | None |  | No
5-55 | Table G3.1 #1, Baseline column: The baseline building design shall be developed by modifying the proposed design as described in Section G3. Except as specifically instructed, all building systems and equipment shall be modeled identically in the proposed design and baseline building design. | Opaque roof surfaces that are not regulated (not part of opaque building envelope) must be modeled with the same thermal emittance and solar reflectance in the baseline as in the proposed design | Baseline RMR | = | Proposed RMR | None |  | No
5-56 | Table G3.1 #1, Baseline column: The baseline building design shall be developed by modifying the proposed design as described in Section G3. Except as specifically instructed, all building systems and equipment shall be modeled identically in the proposed design and baseline building design. | Area of each surface in the baseline is the same as in the proposed design | Baseline RMR | = | Proposed RMR | None |  | No

## Templates
key1 | key2 | key3 | key4 | data_group | data_element | unit_type | units | template-rule-5-2-a | template-rule-5-2-b | template-rule-5-3-a | template-rule-5-3-b | template-rule-5-4-a | template-rule-5-4-b | template-rule-5-5-a | template-rule-5-5-b | template-rule-5-5-c | template-rule-5-5-d | template-rule-5-5-e | template-rule-5-5-f | template-rule-5-5-g | template-rule-5-6-a | template-rule-5-6-b | template-rule-5-7-a | template-rule-5-7-b | template-rule-5-7-c | template-rule-5-7-d | template-rule-5-7-e | template-rule-5-7-f | template-rule-5-8-a | template-rule-5-8-b | template-rule-5-8-c | template-rule-5-8-d | template-rule-5-8-e | template-rule-5-8-f | template-rule-5-9-a | template-rule-5-9-b | template-rule-5-10-a | template-rule-5-10-b | template-rule-5-11-a | template-rule-5-11-b | template-rule-5-11-c | template-rule-5-11-d | template-rule-5-11-e | template-rule-5-11-f | template-rule-5-11-g | template-rule-5-12-a | template-rule-5-12-b | template-rule-5-13-a | template-rule-5-13-b | template-rule-5-13-c | template-rule-5-13-d | template-rule-5-13-e | template-rule-5-13-f | template-rule-5-13-g | template-rule-5-14-a | template-rule-5-14-b | template-rule-5-15-a | template-rule-5-15-b | template-rule-5-15-c | template-rule-5-15-d | template-rule-5-15-e | template-rule-5-15-f | template-rule-5-15-g | template-rule-5-16-a | template-rule-5-16-b | template-rule-5-17-a | template-rule-5-17-b | template-rule-5-17-c | template-rule-5-17-d | template-rule-5-17-e | template-rule-5-17-f | template-rule-5-17-g | template-rule-5-17-h | template-rule-5-17-i | template-rule-5-17-j | template-rule-5-17-k | template-rule-5-17-l | template-rule-5-18-a | template-rule-5-18-b | template-rule-5-18-c | template-rule-5-18-d | template-rule-5-19-a | template-rule-5-19-b | template-rule-5-19-c | template-rule-5-19-d | template-rule-5-20-a | template-rule-5-20-b | template-rule-5-21-a | template-rule-5-21-b | template-rule-5-22-a | template-rule-5-23-a | template-rule-5-23-b | template-rule-5-24-a | template-rule-5-24-b | template-rule-5-24-c | template-rule-5-24-d | template-rule-5-24-d | template-rule-5-24-e | template-rule-5-24-f | template-rule-5-25-a | template-rule-5-25-b | template-rule-5-26-a | template-rule-5-26-b | template-rule-5-26-c | template-rule-5-26-d | template-rule-5-26-e | template-rule-5-26-f | template-rule-5-27-a | template-rule-5-27-b | template-rule-5-28-a | template-rule-5-28-b | template-rule-5-28-c | template-rule-5-28-d | template-rule-5-29-c | template-rule-5-29-b | template-rule-5-29-c | template-rule-5-30-a | template-rule-5-30-b | template-rule-5-31-a | template-rule-5-31-b | template-rule-5-33-a | template-rule-5-33-b | template-rule-5-33-b | template-rule-5-34-a | template-rule-5-34-b | template-rule-5-35-a | template-rule-5-35-b | template-rule-5-36-a | template-rule-5-36-b | template-rule-5-37-a | template-rule-5-37-b | template-rule-5-37-c | template-rule-5-37-d | template-rule-5-37-e | template-rule-5-37-f | template-rule-5-38-a | template-rule-5-38-b | template-rule-5-38-c | template-rule-5-38-d | template-rule-5-38-e | template-rule-5-38-f | template-rule-5-38-g | template-rule-5-39-a | template-rule-5-39-b | template-rule-5-39-c | template-rule-5-40-a | template-rule-5-40-b | template-rule-5-41-a | template-rule-5-41-b | template-rule-5-41-c | template-rule-5-41-d | template-rule-5-42-a | template-rule-5-42-b | template-rule-5-43-a | template-rule-5-43-b | template-rule-5-43-c | template-rule-5-43-d | template-rule-5-44-a | template-rule-5-44-a | template-rule-5-44-a | template-rule-5-45-b | template-rule-5-45-b | template-rule-5-46-a | template-rule-5-46-b | template-rule-5-47-a | template-rule-5-47-b | template-rule-5-47-c | template-rule-5-47-d | template-rule-5-47-e | template-rule-5-47-f | template-rule-5-47-g | template-rule-5-47-h | template-rule-5-48-a | template-rule-5-48-b | template-rule-5-49-a | template-rule-5-49-b | template-rule-5-49-c | template-rule-5-49-d | template-rule-5-50-a | template-rule-5-50-b | template-rule-5-50-c | template-rule-5-51-c | template-rule-5-51-c | template-rule-5-51-c | template-rule-5-51-d | template-rule-5-52-a | template-rule-5-52-b | template-rule-5-53-a | template-rule-5-53-b | template-rule-5-53-c | template-rule-5-53-d | template-rule-5-53-d | template-rule-5-53-e | template-rule-5-53-f | template-rule-5-53-g | template-rule-5-53-h | template-rule-5-53-i | template-rule-5-53-j | template-rule-5-53-k | template-rule-5-53-l | template-rule-5-54-a | template-rule-5-54-b | template-rule-5-55-a | template-rule-5-55-b | template-rule-5-55-b | template-rule-5-56-a | template-rule-5-56-b
id | [7 empty] | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 |  | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 |  |  | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 |  |  | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 |  |  | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229
buildings[0] | id | [6 empty] | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 |  | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 |  |  | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 |  |  | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 |  |  | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1
buildings[0] | building_open_schedule | [6 empty] | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 |  | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 |  |  | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 |  |  | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 |  |  | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1
buildings[0] | has_site_shading | [177 empty] | FALSE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE
buildings[0] | is_all_new | [76 empty] | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
JSON_PATH:building_segments[0] | id | [6 empty] | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 |  | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 |  |  | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 |  |  | segment_1 | segment_1 | segment_1 | segment_1 | [9 empty] | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1
JSON_PATH:building_segments[1] | id | [84 empty] | segment_2
JSON_PATH:building_segments[0] | area_type_vertical_fenestration | [76 empty] | SCHOOL_PRIMARY | SCHOOL_PRIMARY | WAREHOUSE_NONREFRIGERATED | WAREHOUSE_NONREFRIGERATED | OTHER | OTHER | OTHER | OTHER | OFFICE_MEDIUM
JSON_PATH:building_segments[1] | area_type_vertical_fenestration | [84 empty] | HOTEL_MOTEL_SMALL
JSON_PATH:zones[0] | id | [6 empty] | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | [8 empty] | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 |  | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 |  |  | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 |  |  | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | [8 empty] | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1
JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule | [6 empty] | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1
JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule | [6 empty] | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1
JSON_PATH:zones[0] | served_by_heating_ventilation_air_conditioning_systems | [76 empty] | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | [59 empty] | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 |  |  |  |  | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | [34 empty] | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 |  |  | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1
JSON_PATH:zones[0] | spaces | [91 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1
JSON_PATH:zones[0] | surfaces | [91 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 1
JSON_PATH:infiltration | id | [159 empty] | infiltration_1 | infiltration_1 |  |  | infiltration_1 | infiltration_1 | infiltration_1 | infiltration_1 | infiltration_1 | infiltration_1 | infiltration_1 | infiltration_1 |  |  | infiltration_1 | infiltration_1 | infiltration_1 | infiltration_1
JSON_PATH:infiltration | multiplier_schedule
JSON_PATH:infiltration | measured_air_leakage_rate | [163 empty] | 1.4158 | 0.8495 | 0.8495 | 1.4158 | 1.4158 | 0.8495 | 0.8495 | 1.4158 |  |  | 0.09514 | 0.8495 | 0.09514 | 0.8495
JSON_PATH:zones[0] | infiltration_modeling_method_type | [156 empty] | WEATHER_DRIVEN | PRESSURE_BASED | CONSTANT
JSON_PATH:surfaces[0] | id | [6 empty] | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 |  | surface_1 | surface_1 |  |  |  | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 |  |  | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 |  |  | surface_1 | surface_1 | surface_1 | surface_1 | [10 empty] | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 |  |  |  | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | [7 empty] | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 |  |  | surface_1 | surface_1 | surface_1 | surface_1 | [9 empty] | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 |  |  | surface_1 | surface_1 | surface_1 | surface_1 | surface_1
JSON_PATH:surfaces[0] | azimuth | [6 empty] | 20
JSON_PATH:surfaces[0] | adjacent_to | [8 empty] | EXTERIOR | EXTERIOR |  |  | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR |  |  | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | [6 empty] | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR |  |  | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR |  |  | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | [10 empty] | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR |  |  |  | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | [7 empty] | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR |  |  | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | [9 empty] | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR |  |  | EXTERIOR | EXTERIOR | EXTERIOR
JSON_PATH:surfaces[0] | does_cast_shade | [8 empty] | FALSE | TRUE
JSON_PATH:surfaces[0] | tilt | [10 empty] | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 80 | 80 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 180 | 180 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  |  |  |  | 90 | 90 | 90 | 90 | 180 | 180 | 180 | 180 | 90 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 90 |  | 90 | 90 |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  |  | 90 | 90 | 90 | 90 | 90 | 90 | [16 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 50 | 50 | 20 | 20 | 20 | 20 | 50 | 50 | 59 | 59 | 59 | 59 | [45 empty] | 50 | 50 | 50
JSON_PATH:surfaces[0] | area | [76 empty] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 |  | 1000 | 1000 | [34 empty] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | [22 empty] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 |  |  | 1000 | 1000 | 1000 | 1000 | [27 empty] | 100 | 100
JSON_PATH:surfaces[0] | subsurfaces | [84 empty] | 1 |  | 3 | 3 | [20 empty] | 1 | 1 | 1 | 1 | [12 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
JSON_PATH:surfaces[0] | subsurfaces[0] | id | [75 empty] | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 |  | subsurface_1 | subsurface_1 |  | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | [42 empty] | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1
JSON_PATH:surfaces[0] | subsurfaces[0] | classification | [75 empty] | Window | WINDOW | WINDOW | WINDOW | WINDOW | [105 empty] | SWINGING_DOOR | SWINGING_DOOR | SWINGING_DOOR | SWINGING_DOOR | SWINGING_DOOR | SWINGING_DOOR | SWINGING_DOOR | NONSWINGING_DOOR | NONSWINGING_DOOR | NONSWINGING_DOOR | NONSWINGING_DOOR | NONSWINGING_DOOR | NONSWINGING_DOOR | NONSWINGING_DOOR | NONSWINGING_DOOR
JSON_PATH:surfaces[0] | subsurfaces[0] | glazed_area | [75 empty] | 220 | 220 | 60 | 60 |  |  |  |  | 150 | [5 empty] | 200 | [17 empty] | 500 | 500 | 500 | 500 | [10 empty] | 65 | 65 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 150 | 60 | 60 | 150 | 150
JSON_PATH:surfaces[0] | subsurfaces[0] | opaque_area | [75 empty] | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 160 |  | 0 | 0 |  |  | 0 | [17 empty] | 100 |  | 120 | 120 | [10 empty] | 20 | 20 | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 10 | 10 | 50 | 50
JSON_PATH:surfaces[0] | subsurfaces[0] | u_factor | [90 empty] | 3.236 | 3.536 | 3.236 | 6.927 | 6.927 | 6.927 | 6.927 | 3.125 | [9 empty] | 6.75 | 6.75 |  | 6.75 | [16 empty] | 3.293 | 3.9178 | 3.9178 | 3.9378 | 7.722 | 3.293 | [52 empty] | 2.839 | 3.9746 | 3.9746 | 3.9746 | 3.9746 | 3.9746 | 2.839 | 2.839 | 3.9746 | 2.839 | 3.839 | 8.2331 | 2.839
JSON_PATH:surfaces[0] | subsurfaces[0] | solar_heat_gain_coefficient | [99 empty] | 0.39 | 0.4 | 0.39 | 0.4 | 0.4 | 0.39 | 0.35 |  | 0.5 | 0.5 | 0.5 | 0.5 | [22 empty] | 0.36 | 0.19 | 0.19 | 0.49 | 0.39 | 0.55 | 0.39
JSON_PATH:surfaces[0] | subsurfaces[0] | has_shading_overhang | [111 empty] | FALSE | TRUE | FALSE | TRUE | TRUE
JSON_PATH:surfaces[0] | subsurfaces[0] | has_shading_sidefins | [111 empty] | FALSE | FALSE | TRUE | FALSE
JSON_PATH:surfaces[0] | subsurfaces[0] | has_manual_interior_shades | [116 empty] | TRUE
JSON_PATH:surfaces[0] | subsurfaces[0] | has_automatic_shades | [118 empty] | TRUE | FALSE | FALSE
JSON_PATH:surfaces[0] | subsurfaces[0] | dynamic_glazing_type | [140 empty] | MANUAL_DYNAMIC | AUTOMATIC_DYNAMIC | AUTOMATIC_DYNAMIC
JSON_PATH:surfaces[0] | surface_optical_properties[0] | id | [143 empty] | surface_optical_properties_1 | surface_optical_properties_1 | surface_optical_properties_1 | surface_optical_properties_1 | surface_optical_properties_1 | surface_optical_properties_1 | surface_optical_properties_1 | surface_optical_properties_1 | surface_optical_properties_1 | surface_optical_properties_1 | surface_optical_properties_1 | surface_optical_properties_1 | [45 empty] | surface_optical_properties_1 | surface_optical_properties_1 | surface_optical_properties_1
JSON_PATH:surfaces[0] | surface_optical_properties[0] | absorptance_thermal_exterior | [143 empty] | 0.1 | 0.9 | 0.8 | 0.9 | [53 empty] | 0.5 | 0.5 | 0.5
JSON_PATH:surfaces[0] | surface_optical_properties[0] | absorptance_solar_exterior | [149 empty] | 0.7 | 0.7 | 0.7 | 0.8 | 0.8 | 0.8 | [45 empty] | 0.5 | 0.5 | 0.5
JSON_PATH:construction | id | [6 empty] | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1 | construction_1
JSON_PATH:construction | surface_construction_input_option | [10 empty] | LAYERS | SIMPLIFIED | [9 empty] | LAYERS | SIMPLIFIED | LAYERS | LAYERS | LAYERS | LAYERS | [8 empty] | LAYERS | SIMPLIFIED | [7 empty] | LAYERS | SIMPLIFIED | [7 empty] | LAYERS | SIMPLIFIED
JSON_PATH:construction | c_factor | [27 empty] | 6.473 | 6.473 | 0.363 | 6.473 | 6.473 | 0.363 | [35 empty] | 1.25 |  | 1.25
JSON_PATH:construction | f_factor | [55 empty] | 1.263 | 1.263 | 0.392 | 1.263 | 0.376 | 1.263 | 0.376 | 1.5 | [9 empty] | 1.25 |  | 1.25
JSON_PATH:construction | u_factor | [12 empty] | 0.358 | 0.358 | 1.238 | 0.358 | 1.238 | 1.238 | 0.358 | 1.5 | 1.5 | [12 empty] | 1.5 | 1.5 |  |  | 0.363 | 0.363 | 1.238 | 0.704 | 1.238 | 0.704 | 0.358 |  |  | 0.363 | 0.363 | 1.238 | 0.704 | 1.238 | 0.704 | 0.704 | [11 empty] | 1.25 |  | 1.25
JSON_PATH:construction | primary_layers.material[0].thickness | [21 empty] | 8 |  | 9 | 8 | 8 | 8
JSON_PATH:construction | primary_layers.material[0].thermal_conductivity | [21 empty] | 7.2 |  | 7.2 | 8 | 7.2 | 7.2
JSON_PATH:construction | primary_layers.material[0].density | [21 empty] | 115 |  | 115 | 115 | 120 | 115
JSON_PATH:construction | primary_layers.material[0].specific_heat | [21 empty] | equivalent to HC=15.3?? |  | equivalent to HC=15.3?? | equivalent to HC=15.3?? | equivalent to HC=15.3?? | equivalent to HC=8??
JSON_PATH:surfaces[1] | id | [6 empty] | surface_2 | surface_2 | surface_2 | surface_2 | [66 empty] | surface_2 | surface_2 | surface_2 | surface_2 | surface_2 | surface_2 | surface_2 | surface_2 | surface_2 |  | surface_2 | surface_2 | [34 empty] | surface_2 | surface_2 | surface_2 | surface_2 | surface_2 | surface_2 | [35 empty] | surface_2 | surface_2 | surface_2 | surface_2 | surface_2 | surface_2 | surface_2 | surface_2 |  |  | surface_2 | surface_2 | surface_2 | surface_2 | [27 empty] | surface_2 | surface_2
JSON_PATH:surfaces[1] | adjacent_to | [76 empty] | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | [37 empty] | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | [35 empty] | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND | GROUND |  |  | GROUND | GROUND | GROUND | GROUND
JSON_PATH:surfaces[1] | tilt | [76 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 75 | 75 | [34 empty] | 50 | 50 | 50 | 50 | 50 | 50
JSON_PATH:surfaces[1] | area | [76 empty] | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  | 1000 | 1000 | [34 empty] | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | [35 empty] | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  |  | 2000 | 2000 | 2000 | 2000 | [27 empty] | 150 | 150
JSON_PATH:surfaces[1] | azimuth | [6 empty] | 190 | 190
JSON_PATH:surfaces[1] | does_cast_shade | [8 empty] | TRUE | TRUE
JSON_PATH:surfaces[1] | subsurfaces[0] | id | [75 empty] | subsurface_2 | subsurface_2 | subsurface_2 | subsurface_2 | subsurface_2 | subsurface_2 | subsurface_2 | subsurface_2 | subsurface_2 |  | subsurface_2 | subsurface_2 |  |  | subsurface_2 | [7 empty] | subsurface_2 | subsurface_2 | [25 empty] | subsurface_2 | subsurface_2 | subsurface_2
JSON_PATH:surfaces[1] | subsurfaces[0] | classification | [75 empty] | DOOR | DOOR | WINDOW | WINDOW | WINDOW | Window | Window | Window | Window | [5 empty] | 200 | [7 empty] | 200 | 200
JSON_PATH:surfaces[1] | subsurfaces[0] | glazed_area | [75 empty] | 400 | 400 | 100 | 100 | 700 | 700 | 200 | [7 empty] | 50 | [7 empty] | 50 | 50 | [25 empty] | 900 | 900 | 900
JSON_PATH:surfaces[1] | subsurfaces[0] | opaque_area | [75 empty] | 40 | 60 | 20 | 20 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | [37 empty] | 100 | 100 | 100
JSON_PATH:surfaces[2] | id | [8 empty] | surface_3 | surface_3
JSON_PATH:surfaces[2] | adjacent_to | [8 empty] | IDENTICAL | IDENTICAL
JSON_PATH:surfaces[2] | subsurfaces[0] | classification
JSON_PATH:surfaces[2] | subsurfaces[0] | glazed_area
JSON_PATH:surfaces[2] | subsurfaces[0] | opaque_area
JSON_PATH:surfaces[2] | does_cast_shade | [8 empty] | TRUE | TRUE
JSON_PATH:surfaces[3] | id | [8 empty] | surface_4 | surface_4
JSON_PATH:surfaces[3] | adjacent_to | [8 empty] | GROUND | GROUND
JSON_PATH:surfaces[3] | does_cast_shade | [8 empty] | TRUE | TRUE
JSON_PATH:surfaces[4] | id | [8 empty] | surface_5 | surface_5
JSON_PATH:surfaces[4] | adjacent_to | [8 empty] | UNDEFINED | UNDEFINED
JSON_PATH:surfaces[4] | does_cast_shade | [8 empty] | FALSE | FALSE
JSON_PATH:weather[0] | climate_zone | [12 empty] | 4A | 4A | 4A | 4A | 4A | 4A | 4A |  |  |  | 4A |  |  |  |  | 4A | 4A | 4A | 4A | 4A | 4A |  |  |  |  | 4A | 4A | 4A | 4A | 4A | 4A | 4A |  |  | 4A | 4A | 4A | 4A | 4A | 4A | 4A |  |  | 4A | 4A | 4A | 4A | 4A | 4A | 4A |  |  | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | [15 empty] | 4A | 4A | 4A | 4A | 4A | 4A | 4A |  |  | 4A | 4A | 4A | 4A | 4A | 4A |  |  | 4A | 4A | 4A | 4A | [10 empty] | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A | [11 empty] | 4A | 4A | 4A | 4A | 4A | 4A | 4A | 4A |  |  | 4A | 4A | 4A | 4A | [9 empty] | 7A | 7A | 7A | 7A | 7A | 7A | 7A | 7A | 7A | 7A | 7A | 7A | 7A |  |  | 4A | 4A | 4A
JSON_PATH:heating_ventilation_air_conditioning_systems[0] | id | [12 empty] | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 |  |  |  | heating_ventilation_air_conditioning_systems_1 |  |  |  |  | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 |  |  |  |  | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 |  |  | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 |  |  | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 |  |  | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | [6 empty] | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 |  |  | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 |  |  | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | [10 empty] | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | [11 empty] | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 |  |  | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | [9 empty] | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 |  |  | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1
JSON_PATH:heating_ventilation_air_conditioning_systems[0] | simulation_result_sensible_cool_capacity | [12 empty] | 5 | 12 | 5 | 5 | 5 | 5 | 5 |  |  |  | 5 |  |  |  |  | 5 | 1 | 5 | 5 | 5 | 5 |  |  |  |  | 5 | 12 | 5 | 5 | 5 | 5 | 5 |  |  | 5 | 12 | 5 | 5 | 5 | 5 | 5 |  |  | 5 | 11 | 5 | 5 | 5 | 5 | 5 |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 12 | 12 | 0 | 0 | 15 | 15 | 15 | 15 | 12 | [6 empty] | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 |  |  | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 |  |  | 9000 | 9000 | 9000 | 9000 | [10 empty] | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [11 empty] | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 |  |  | 10000 | 10000 | 10000 | 10000 | [9 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  |  | 20 | 20 | 20
JSON_PATH:heating_ventilation_air_conditioning_systems[0] | simulation_result_heat_capacity | [12 empty] | 32 | 30 | 32 | 32 | 32 | 12 | 12 |  |  |  | 12 |  |  |  |  | 35 | 12 | 35 | 35 | 30 | 30 |  |  |  |  | 32 | 30 | 32 | 32 | 32 | 12 | 12 |  |  | 32 | 30 | 32 | 32 | 32 | 12 | 12 |  |  | 32 | 30 | 32 | 32 | 32 | 12 | 12 |  |  | 10 | 10 | 15 | 15 | 10 | 10 | 15 | 15 | 10 | 10 | 15 | 15 | 35 | 35 | 15 | 15 | 35 | 35 | 35 | 35 | 35 | [6 empty] | 32000 | 32000 | 32000 | 32000 | 32000 | 30000 | 30000 |  |  | 32000 | 32000 | 32000 | 32000 | 30000 | 30000 |  |  | 30000 | 30000 | 30000 | 30000 | [10 empty] | 33000 | 33000 | 33000 | 33000 | 33000 | 33000 | 32000 | 32000 | 32000 | 32000 | 30000 | 30000 | 32000 | 32000 | 32000 | 32000 | 32000 | 30000 | 30000 | 30000 | 30000 | 30000 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | [11 empty] | 32000 | 32000 | 32000 | 32000 | 30000 | 30000 | 30000 | 30000 |  |  | 30000 | 30000 | 30000 | 30000 | [9 empty] | 51 | 51 | 51 | 51 | 51 | 50 | 50 | 50 | 51 | 51 | 51 | 50 | 50 |  |  | 50 | 50 | 50
JSON_PATH:heating_ventilation_air_conditioning_systems[1] | id | [84 empty] | heating_ventilation_air_conditioning_systems_2
JSON_PATH:heating_ventilation_air_conditioning_systems[1] | simulation_result_sensible_cool_capacity | [84 empty] | 15
JSON_PATH:heating_ventilation_air_conditioning_systems[1] | simulation_result_heat_capacity | [84 empty] | 35
JSON_PATH:spaces[0] | id | [12 empty] | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 |  |  |  | space_1 |  |  |  |  | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 |  |  | space_1 |  | space_1 | space_1 | space_1 | space_1 | space_1 |  |  |  |  | space_1 | space_1 | space_1 | space_1 | space_1 |  |  |  |  | space_1 | space_1 | space_1 | space_1 | space_1 | [31 empty] | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 |  |  | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | [22 empty] | space_1 | space_1 | space_1 | space_1 |  |  | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | [42 empty] | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1
JSON_PATH:spaces[0] | lighting_space_type | [12 empty] | DWELLING_UNIT | DWELLING_UNIT | DWELLING_UNIT | Corridor | Corridor | [10 empty] | GUEST_ROOM | GUEST_ROOM | GUEST_ROOM | OFFICE_ENCLOSED |  |  |  |  | DWELLING_UNIT |  | DWELLING_UNIT | DWELLING_UNIT | DWELLING_UNIT | CLASSROOM_LECTURE_HALL_TRAINING_ROOM_ALL_OTHER | CLASSROOM_LECTURE_HALL_TRAINING_ROOM_ALL_OTHER |  |  |  |  | DWELLING_UNIT | DWELLING_UNIT | DWELLING_UNIT | CLASSROOM_LECTURE_HALL_TRAINING_ROOM_ALL_OTHER | CLASSROOM_LECTURE_HALL_TRAINING_ROOM_ALL_OTHER |  |  |  |  | DORMITORY_LIVING_QUARTERS | DORMITORY_LIVING_QUARTERS | DORMITORY_LIVING_QUARTERS | WORKSHOP | STAIRWELL | [31 empty] | DWELLING_UNIT | DWELLING_UNIT | STAIRWELL | STAIRWELL | STAIRWELL | STAIRWELL | STAIRWELL |  |  | DWELLING_UNIT | DWELLING_UNIT | STAIRWELL | STAIRWELL | STAIRWELL | STAIRWELL | [22 empty] | DWELLING_UNIT | DWELLING_UNIT | OFFICE | OFFICE |  |  | DWELLING_UNIT | DWELLING_UNIT | STAIRWELL | STAIRWELL | STAIRWELL | STAIRWELL | STAIRWELL | STAIRWELL | STAIRWELL | STAIRWELL | [42 empty] | DWELLING_UNIT | DWELLING_UNIT | DWELLING_UNIT | CLASSROOM | CLASSROOM | CLASSROOM | CLASSROOM | DWELLING_UNIT | DWELLING_UNIT | CLASSROOM | CLASSROOM | CLASSROOM | CLASSROOM
JSON_PATH:spaces[0] | status_type
EXISTING
Note on AW25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rule description says this is a floor-- these appear like walls with 90 degree tilts.
Note on AX25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rule description says this is a floor-- these appear like walls with 90 degree tilts.
Note on AY25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rule description says this is a floor-- these appear like walls with 90 degree tilts.
Note on AZ25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rule description says this is a floor-- these appear like walls with 90 degree tilts.
Note on BA25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rule description says this is a floor-- these appear like walls with 90 degree tilts.
Note on BB25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rule description says this is a floor-- these appear like walls with 90 degree tilts.
Note on BC25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rule description says this is a floor-- these appear like walls with 90 degree tilts.
Note on BC46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Same as f? Doesn't make sense. This U-factor should fail

## TCDs
key1 | key2 | key3 | key4 | key5 | data_group | data_element | unit_type | units | rule-5-34-a | rule-5-34-b | rule-5-35-a | rule-5-35-b | rule-5-36-a | rule-5-36-b | rule-5-37-a | rule-5-37-b | rule-5-37-c | rule-5-37-d | rule-5-37-e | rule-5-37-f | rule-5-38-a | rule-5-38-b | rule-5-38-c | rule-5-38-d | rule-5-38-e | rule-5-38-f | rule-5-38-g | rule-5-39-a | rule-5-39-b | rule-5-39-c
Section | [8 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Rule | [8 empty] | 34 | 34 | 35 | 35 | 36 | 36 | 37 | 37 | 37 | 37 | 37 | 37 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 39 | 39 | 39
Test | [8 empty] | a | b | a | b | a | b | a | b | c | d | e | f | a | b | c | d | e | f | g | a | b | c
Notes
test_description | [8 empty] | Building area type = "school (primary)"; building includes a conditioned zone that has two exterior walls with windows. Baseline fenestration area is established correctly. | Building area type = "school (primary)"; building includes a conditioned zone that has two exterior walls with windows. Baseline fenestration area is established correctly. | Building includes a conditioned zone that has two roof surfaces one of which has skylights. Skylight area in the proposed design exceeds 3% of total roof area. Baseline skylight area is correctly modeled as equal to 3% of the total roof area | Building includes a conditioned zone that has two roof surfaces both of which have skylights. Skylight area in the user model exceeds 3% of total roof area. Baseline skylight area is not modeled as equal to 3% of the total roof area, which is incorrect | Building includes a conditioned zone that has two roof surfaces both of which have skylights. Baseline skylight area is allocated to roof surfaces in the same proportion as in the proposed design | Building includes a conditioned zone that has two roof surfaces both of which have skylights. Baseline skylight area is allocated to roof surfaces in the same proportion as in the proposed design | Building is located in climate zone 4A. It includes a semiheated zone based on heating and cooling capacity of the HVAC system that servies it. Skylight area in the building is 0%-2.0%. The baseline skylight U-factor is established correctly. | Building is located in climate zone 4A. It includes a semiheated zone based on heating and cooling capacity of the HVAC system that servies it. Skylight area in the building is 0%-2.0%. The baseline skylight U-factor is established correctly. | Building is located in climate zone 4A. It includes a semiheated zone based on heating and cooling capacity of the HVAC system that servies it. Skylight area in the building is 0%-2.0%. The baseline skylight U-factor is established correctly. | Building is located in climate zone 4A. It includes a semiheated zone based on heating and cooling capacity of the HVAC system that servies it. Skylight area in the building is 0%-2.0%. The baseline skylight U-factor is established correctly. | Building is located in climate zone 4A. It includes a semiheated zone based on heating and cooling capacity of the HVAC system that servies it. Skylight area in the building is 0%-2.0%. The baseline skylight U-factor is established correctly. | Building is located in climate zone 4A. It includes a semiheated zone based on heating and cooling capacity of the HVAC system that servies it. Skylight area in the building is 0%-2.0%. The baseline skylight U-factor is established correctly. | Building is located in climate zone 4A. It includes a zone with residential occupancy type that is conditioned based on heating and cooling capacity of the HVAC system that servies it. Skylight area in the building is 0%-2.0%. The baseline skylight SHGC is established correctly. | Building is located in climate zone 4A. It includes a zone with residential occupancy type that is conditioned based on heating and cooling capacity of the HVAC system that servies it. Skylight area in the building is 0%-2.0%. The baseline skylight SHGC is not established correctly. | Building is located in climate zone 4A. It includes a zone with residential occupancy type that is conditioned based on heating and cooling capacity of the HVAC system that servies it. Skylight area in the building is 0%-2.0%. The baseline skylight SHGC is not established correctly. | Building is located in climate zone 4A. It includes a space that has non-residential occupancy type and is conditioned based on heating and cooling capacity of the HVAC system that servies it. Skylight area in the building is 0-2.0%. The baseline vertical fenestration SHGC for the space is established correctly. | Building is located in climate zone 4A. It includes a space that has non-residential occupancy type and is conditioned based on heating and cooling capacity of the HVAC system that servies it. Skylight area in the building is 2.1%+. The baseline vertical fenestration SHGC for the space is established correctly. | A space is semiheated based on heating and cooling capacity of the HVAC system that servies it. Building is located in climate zone 4A. Skylight area in the building is 2.1%+. The baseline skylight SHGC for the space is established correctly. | A space is semiheated based on heating and cooling capacity of the HVAC system that servies it. Building is located in climate zone 4A. Skylight area in the building is 2.1%+. The baseline skylight SHGC for the space is not established correctly. | subsurface has manual dynamic glazing in both user model and proposed model; manual check is required to verify that SHCG and VT were modeled correctly | subsurface has automatic dynalic glazing in both user model and proposed model | subsurface has diferent type of dynamic glazing in the proposed design vs user model
expected_rule_outcome | [8 empty] | fail | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | pass | pass | pass | pass | manual_check | pass | pass
standard | rule_id | [7 empty] | 5-34 | 5-34 | 5-35 | 5-35 | 5-36 | 5-36 | 5-37 | 5-37 | 5-37 | 5-37 | 5-37 | 5-37 | 5-38 | 5-38 | 5-38 | 5-38 | 5-38 | 5-38 | 5-38 | 5-39 | 5-39 | 5-39
standard | ruleset_reference | [7 empty] | Table G3.1#5 baselnid column e. e. Skylights and Glazed Smoke Vents. Skylight area shall be equal to that in the proposed design or 3%, whichever is smaller. | Table G3.1#5 baselnid column e. e. Skylights and Glazed Smoke Vents. Skylight area shall be equal to that in the proposed design or 3%, whichever is smaller. | Table G3.1#5 baselnid column e: If the skylight area of the proposed design is greater than 3%, baseline skylight area shall be decreased by an identical percentage in all roof components in which skylights are located to reach 3%. | Table G3.1#5 baselnid column e: If the skylight area of the proposed design is greater than 3%, baseline skylight area shall be decreased by an identical percentage in all roof components in which skylights are located to reach 3%. | Table G3.1#5 baselnid column e: Skylight orientation and tilt shall be the same as in the proposed design. | Table G3.1#5 baselnid column e: Skylight orientation and tilt shall be the same as in the proposed design. | Table G3.1#5 baseline column e: Skylight U-factor … shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Table G3.1#5 baseline column e: Skylight U-factor … shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Table G3.1#5 baseline column e: Skylight U-factor … shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Table G3.1#5 baseline column e: Skylight U-factor … shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Table G3.1#5 baseline column e: Skylight U-factor … shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Table G3.1#5 baseline column e: Skylight U-factor … shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Table G3.1#5 baseline column e: Skylight… SHGC properties shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Table G3.1#5 baseline column e: Skylight… SHGC properties shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Table G3.1#5 baseline column e: Skylight… SHGC properties shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Table G3.1#5 baseline column e: Skylight… SHGC properties shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Table G3.1#5 baseline column e: Skylight… SHGC properties shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Table G3.1#5 baseline column e: Skylight… SHGC properties shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Table G3.1#5 baseline column e: Skylight… SHGC properties shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Table G3.1 #5 Proposed column a5: Automatically controlled dynamic glazing may be modeled. Manually controlled dynamic glazing shall use the average of the minimum and maximum SHGC and VT. | Table G3.1 #5 Proposed column a5: Automatically controlled dynamic glazing may be modeled. Manually controlled dynamic glazing shall use the average of the minimum and maximum SHGC and VT. | Table G3.1 #5 Proposed column a5: Automatically controlled dynamic glazing may be modeled. Manually controlled dynamic glazing shall use the average of the minimum and maximum SHGC and VT.
standard | rule_description | [7 empty] | If skylight area in the proposed desing is 3% or less of the roof surface, the skylight area shall be equal to that in the proposed design. | If skylight area in the proposed desing is 3% or less of the roof surface, the skylight area shall be equal to that in the proposed design. | If the skylight area of the proposed design is greater than 3%, baseline skylight area shall be decreased by an identical percentage in all roof components in which skylights are located to reach 3%. | If the skylight area of the proposed design is greater than 3%, baseline skylight area shall be decreased by an identical percentage in all roof components in which skylights are located to reach 3%. | Skylight area must be allocated to surfaces in the same proportion in the baseline as in the proposed design; Skylight orientation and tilt shall be the same as in the proposed design. | Skylight area must be allocated to surfaces in the same proportion in the baseline as in the proposed design; Skylight orientation and tilt shall be the same as in the proposed design. | Skylight U-factors for residential, non-residential and semiheated spaces in the baseline model must match the appropriate requirements in Table G3.4-1 through G3.4-8 | Skylight U-factors for residential, non-residential and semiheated spaces in the baseline model must match the appropriate requirements in Table G3.4-1 through G3.4-8 | Skylight U-factors for residential, non-residential and semiheated spaces in the baseline model must match the appropriate requirements in Table G3.4-1 through G3.4-8 | Skylight U-factors for residential, non-residential and semiheated spaces in the baseline model must match the appropriate requirements in Table G3.4-1 through G3.4-8 | Skylight U-factors for residential, non-residential and semiheated spaces in the baseline model must match the appropriate requirements in Table G3.4-1 through G3.4-8 | Skylight U-factors for residential, non-residential and semiheated spaces in the baseline model must match the appropriate requirements in Table G3.4-1 through G3.4-8 | Skylight SHGC properties shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Skylight SHGC properties shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Skylight SHGC properties shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Skylight SHGC properties shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Skylight SHGC properties shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Skylight SHGC properties shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Skylight SHGC properties shall match the appropriate requirements in Tables G3.4-1 through G3.4-8 using the value and the applicable skylight percentage. | Automatically controlled dynamic glazing may be modeled. Manually controlled dynamic glazing shall use the average of the minimum and maximum SHGC and VT. | Automatically controlled dynamic glazing may be modeled. Manually controlled dynamic glazing shall use the average of the minimum and maximum SHGC and VT. | Automatically controlled dynamic glazing may be modeled. Manually controlled dynamic glazing shall use the average of the minimum and maximum SHGC and VT.
standard | applicable_rmr | [7 empty] | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Proposed RMR | Proposed RMR | Proposed RMR
standard | rule_assertion | bar: a to c
standard | comparison_value | [7 empty] | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value
standard | rule_dependency | [7 empty] | None | None | None | None | None | None | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline skylight area is established correctly (Rules 34,35) | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline skylight area is established correctly (Rules 34,35) | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline skylight area is established correctly (Rules 34,35) | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline skylight area is established correctly (Rules 34,35) | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline skylight area is established correctly (Rules 34,35) | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline skylight area is established correctly (Rules 34,35) | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline skylight area is established correctly (Rules 34,35) | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline skylight area is established correctly (Rules 34,35) | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline skylight area is established correctly (Rules 34,35) | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline skylight area is established correctly (Rules 34,35) | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline skylight area is established correctly (Rules 34,35) | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline skylight area is established correctly (Rules 34,35) | 1. Baseline heating and cooling capacities are established correctly (air-side HVAC rule TBD). This affects baseline space conditioning categories 2. Baseline skylight area is established correctly (Rules 34,35) | None | None | None
standard | mandatory_rule | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
standard | schema_version | [7 empty] | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5 | 0.0.5
template_lookup | [8 empty] | template-rule-5-34-a | template-rule-5-34-b | template-rule-5-35-a | template-rule-5-35-b | template-rule-5-36-a | template-rule-5-36-b | template-rule-5-37-a | template-rule-5-37-b | template-rule-5-37-c | template-rule-5-37-d | template-rule-5-37-e | template-rule-5-37-f | template-rule-5-38-a | template-rule-5-38-b | template-rule-5-38-c | template-rule-5-38-d | template-rule-5-38-e | template-rule-5-38-f | template-rule-5-38-g | template-rule-5-39-a | template-rule-5-39-b | template-rule-5-39-c
rmr_template | user | [7 empty] | a: true; b: true; c: true
rmr_template | proposed | [7 empty] | true | true | true | true | true | true | true | true | true | true | true | true | [7 empty] | true | true | true
rmr_template | baseline | [7 empty] | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true
rmr_template | json_template | id | [6 empty] | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229 | ashrae_229
rmr_template | json_template | buildings[0] | id | [5 empty] | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1 | building_1
rmr_template | json_template | buildings[0] | building_open_schedule | [5 empty] | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1
rmr_template | json_template | buildings[0] | has_site_shading | bar: g to c
rmr_template | json_template | buildings[0] | is_all_new
rmr_template | json_template | JSON_PATH:building_segments[0] | id | [5 empty] | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1 | segment_1
rmr_template | json_template | JSON_PATH:building_segments[1] | id
rmr_template | json_template | JSON_PATH:building_segments[0] | area_type_vertical_fenestration | bar: g to c
rmr_template | json_template | JSON_PATH:building_segments[1] | area_type_vertical_fenestration
rmr_template | json_template | JSON_PATH:zones[0] | id | [5 empty] | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1 | zone_1
rmr_template | json_template | JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule | [5 empty] | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1
rmr_template | json_template | JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule | [5 empty] | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1 | schedule_1
rmr_template | json_template | JSON_PATH:zones[0] | served_by_heating_ventilation_air_conditioning_systems
rmr_template | json_template | JSON_PATH:zones[0] | spaces | bar: g to c
rmr_template | json_template | JSON_PATH:zones[0] | surfaces
rmr_template | json_template | JSON_PATH:infiltration | id | bar: g to c
rmr_template | json_template | JSON_PATH:infiltration | multiplier_schedule
rmr_template | json_template | JSON_PATH:infiltration | measured_air_leakage_rate | bar: g to c
rmr_template | json_template | JSON_PATH:zones[0] | infiltration_modeling_method_type
rmr_template | json_template | JSON_PATH:surfaces[0] | id | [5 empty] | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1 | surface_1
rmr_template | json_template | JSON_PATH:surfaces[0] | azimuth
rmr_template | json_template | JSON_PATH:surfaces[0] | adjacent_to | [5 empty] | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR | EXTERIOR
rmr_template | json_template | JSON_PATH:surfaces[0] | does_cast_shade
rmr_template | json_template | JSON_PATH:surfaces[0] | tilt | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
rmr_template | json_template | JSON_PATH:surfaces[0] | area | [5 empty] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000
rmr_template | json_template | JSON_PATH:surfaces[0] | subsurfaces | bar: g to c
rmr_template | json_template | JSON_PATH:surfaces[0] | subsurfaces[0] | id |  |  |  |  | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1 | subsurface_1
rmr_template | json_template | JSON_PATH:surfaces[0] | subsurfaces[0] | classification | bar: g to c
rmr_template | json_template | JSON_PATH:surfaces[0] | subsurfaces[0] | glazed_area |  |  |  |  | 65 |  | 100 | 100 |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 150 | 60 | 60 | 150 | 150
rmr_template | json_template | JSON_PATH:surfaces[0] | subsurfaces[0] | opaque_area |  |  |  |  | 20 | 20 | 50 | 50 |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 10 | 10 | 50 | 50
rmr_template | json_template | JSON_PATH:surfaces[0] | subsurfaces[0] | u_factor |  |  |  |  | a: 3.293; b: 3.9178; c: 3.9178; d: 3.9378; e: 7.722; f: 3.293
rmr_template | json_template | JSON_PATH:surfaces[0] | subsurfaces[0] | solar_heat_gain_coefficient |  |  |  |  | a: 0.36; b: 0.19; c: 0.19; d: 0.49; e: 0.39; f: 0.55; g: 0.39
rmr_template | json_template | JSON_PATH:surfaces[0] | subsurfaces[0] | has_shading_overhang
rmr_template | json_template | JSON_PATH:surfaces[0] | subsurfaces[0] | has_shading_sidefins | bar: g to c
rmr_template | json_template | JSON_PATH:surfaces[0] | subsurfaces[0] | has_manual_interior_shades
rmr_template | json_template | JSON_PATH:surfaces[0] | subsurfaces[0] | has_automatic_shades | bar: g to c
rmr_template | json_template | JSON_PATH:surfaces[0] | subsurfaces[0] | dynamic_glazing_type |  |  |  |  | a: MANUAL_DYNAMIC; b: AUTOMATIC_DYNAMIC
rmr_template | json_template | JSON_PATH:surfaces[0] | surface_optics[0] | id | bar: g to c
rmr_template | json_template | JSON_PATH:surfaces[0] | surface_optics[0] | absorptance_thermal_exterior
rmr_template | json_template | JSON_PATH:surfaces[0] | surface_optics[0] | absorptance_solar_exterior | bar: g to c
rmr_template | json_template | JSON_PATH:construction | id
rmr_template | json_template | JSON_PATH:construction | surface_construction_input_option | bar: g to c
rmr_template | json_template | JSON_PATH:construction | c_factor
rmr_template | json_template | JSON_PATH:construction | f_factor | bar: g to c
rmr_template | json_template | JSON_PATH:construction | u_factor
rmr_template | json_template | JSON_PATH:construction | primary_layers.material[0].thickness | bar: g to c
rmr_template | json_template | JSON_PATH:construction | primary_layers.material[0].thermal_conductivity
rmr_template | json_template | JSON_PATH:construction | primary_layers.material[0].density | bar: g to c
rmr_template | json_template | JSON_PATH:construction | primary_layers.material[0].specific_heat
rmr_template | json_template | JSON_PATH:surfaces[1] | id | [5 empty] | a: surface_2; b: surface_2; a: surface_2; b: surface_2; a: surface_2; b: surface_2
rmr_template | json_template | JSON_PATH:surfaces[1] | adjacent_to | [5 empty] | a: EXTERIOR; b: EXTERIOR; a: EXTERIOR; b: EXTERIOR; a: EXTERIOR; b: EXTERIOR
rmr_template | json_template | JSON_PATH:surfaces[1] | tilt | [5 empty] | a: 50; b: 50; a: 50; b: 50; a: 50; b: 50
rmr_template | json_template | JSON_PATH:surfaces[1] | area | [5 empty] | a: 2000; b: 2000; a: 2000; b: 2000; a: 2000; b: 2000
rmr_template | json_template | JSON_PATH:surfaces[1] | azimuth | bar: g to c
rmr_template | json_template | JSON_PATH:surfaces[1] | does_cast_shade
rmr_template | json_template | JSON_PATH:surfaces[1] | subsurfaces[0] | id |  |  |  |  | b: subsurface_2; a: subsurface_2; b: subsurface_2
rmr_template | json_template | JSON_PATH:surfaces[1] | subsurfaces[0] | classification
rmr_template | json_template | JSON_PATH:surfaces[1] | subsurfaces[0] | glazed_area |  |  |  |  | b: 900; b: 900
rmr_template | json_template | JSON_PATH:surfaces[1] | subsurfaces[0] | opaque_area |  |  |  |  | b: 100; b: 100
rmr_template | json_template | JSON_PATH:surfaces[2] | id | bar: g to c
rmr_template | json_template | JSON_PATH:surfaces[2] | adjacent_to
rmr_template | json_template | JSON_PATH:surfaces[2] | subsurfaces[0] | classification | bar: g to c
rmr_template | json_template | JSON_PATH:surfaces[2] | subsurfaces[0] | glazed_area
rmr_template | json_template | JSON_PATH:surfaces[2] | subsurfaces[0] | opaque_area | bar: g to c
rmr_template | json_template | JSON_PATH:surfaces[2] | does_cast_shade
rmr_template | json_template | JSON_PATH:surfaces[3] | id | bar: g to c
rmr_template | json_template | JSON_PATH:surfaces[3] | adjacent_to
rmr_template | json_template | JSON_PATH:surfaces[3] | does_cast_shade | bar: g to c
rmr_template | json_template | JSON_PATH:surfaces[4] | id
rmr_template | json_template | JSON_PATH:surfaces[4] | adjacent_to | bar: g to c
rmr_template | json_template | JSON_PATH:surfaces[4] | does_cast_shade
rmr_template | json_template | weather | climate_zone | [5 empty] | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A | CZ4A
rmr_template | json_template | JSON_PATH:heating_ventilation_air_conditioning_systems[0] | id | [5 empty] | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1 | heating_ventilation_air_conditioning_systems_1
rmr_template | json_template | JSON_PATH:heating_ventilation_air_conditioning_systems[0] | simulation_result_sensible_cool_capacity | bar: g to c
rmr_template | json_template | JSON_PATH:heating_ventilation_air_conditioning_systems[0] | simulation_result_heat_capacity
rmr_template | json_template | JSON_PATH:heating_ventilation_air_conditioning_systems[1] | id | bar: g to c
rmr_template | json_template | JSON_PATH:heating_ventilation_air_conditioning_systems[1] | simulation_result_sensible_cool_capacity
rmr_template | json_template | JSON_PATH:heating_ventilation_air_conditioning_systems[1] | simulation_result_heat_capacity | bar: g to c
rmr_template | json_template | JSON_PATH:spaces[0] | id | [11 empty] | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1 | space_1
rmr_template | json_template | JSON_PATH:spaces[0] | lighting_space_type | [11 empty] | DWELLING_UNIT | DWELLING_UNIT | OFFICE | OFFICE |  |  | DWELLING_UNIT | DWELLING_UNIT | STAIRWELL | STAIRWELL | STAIRWELL | STAIRWELL | STAIRWELL | STAIRWELL | STAIRWELL | STAIRWELL
rmr_template | json_template | JSON_PATH:spaces[0] | status_type
rmr_template | json_template | JSON_PATH:spaces[0] | occupant_multiplier_schedule | [11 empty] | occupant_multiplier_schedule_1 | occupant_multiplier_schedule_1 | occupant_multiplier_schedule_1 | occupant_multiplier_schedule_1 | occupant_multiplier_schedule_1 | occupant_multiplier_schedule_1 | occupant_multiplier_schedule_1 | occupant_multiplier_schedule_1 | occupant_multiplier_schedule_1 | occupant_multiplier_schedule_1 | occupant_multiplier_schedule_1 | occupant_multiplier_schedule_1 | occupant_multiplier_schedule_1 | occupant_multiplier_schedule_1 | occupant_multiplier_schedule_1 | occupant_multiplier_schedule_1
rmr_transformations | user | JSON_PATH:surfaces[0] | azimuth
rmr_transformations | user | JSON_PATH:construction | u_factor
rmr_transformations | user | JSON_PATH:construction | f_factor
rmr_transformations | user | JSON_PATH:surfaces[0] | subsurfaces[0] | dynamic_glazing_type |  |  |  |  | c: MANUAL_DYNAMIC
rmr_transformations | proposed | JSON_PATH:surfaces[0] | azimuth
rmr_transformations | proposed | JSON_PATH:construction | u_factor
rmr_transformations | proposed | JSON_PATH:construction | c_factor
rmr_transformations | proposed | JSON_PATH:construction | f_factor
rmr_transformations | proposed | JSON_PATH:surfaces[0] | subsurfaces[0] | glazed_area |  |  |  |  | b: 65; a: 100; b: 100; a: 100; b: 100
rmr_transformations | proposed | JSON_PATH:surfaces[0] | subsurfaces[0] | opaque_area |  |  |  |  | a: 50; b: 50; a: 50; b: 50
rmr_transformations | proposed | JSON_PATH:surfaces[1] | subsurfaces[0] | glazed_area |  |  |  |  | a: 900
rmr_transformations | proposed | JSON_PATH:surfaces[1] | subsurfaces[0] | opaque_area
rmr_transformations | proposed | JSON_PATH:surfaces[0] | subsurfaces[0] | dynamic_glazing_type |  |  |  |  | c: AUTOMATIC_DYNAMIC
rmr_transformations | baseline | JSON_PATH:construction | u_factor
rmr_transformations | baseline | JSON_PATH:construction | c_factor
rmr_transformations | baseline | JSON_PATH:construction | f_factor
rmr_transformations | baseline | JSON_PATH:surfaces[0] | subsurfaces[0] | glazed_area |  |  |  |  | b: 70; a: 60; b: 60; a: 50; b: 50
rmr_transformations | baseline | JSON_PATH:surfaces[1] | subsurfaces[0] | glazed_area |  |  |  |  | a: 450
rmr_transformations | proposed | JSON_PATH:surfaces[1] | subsurfaces[0] | opaque_area |  |  |  |  | a: 100
rmr_transformations | proposed | JSON_PATH:surfaces[0] | subsurfaces[0] | opaque_area |  |  |  |  | a: 30; b: 30; a: 25; b: 25

## TCD_old (hidden)
appendix_g_section_id | rule_id | test_id | case_number | rule_description | test_outcome | user_rmr_xpath | test_type | target_rmr | test_target | target_id | target_value
15 | 1 | a | 1 | Number of transformers modeled in User RMR and Baseline RMR are the same | pass | building/transformers/.. | num_of_elements_equal_to | baseline | rmr | triplet_101 | building/transformers/..
15 | 1 | b | 1 | Number of transformers modeled in User RMR and Baseline RMR are the same | fail | building/transformers/.. | num_of_elements_equal_to | baseline | rmr | triplet_102 | building/transformers/..
15 | 6 | a | 1 | Transformer efficiency reported in User RMR equals Table 8.4.4 | pass | building/transformer/transformer/type | value_equal_to | user | self | triplet_101 | Drytype
15 | 6 | a | 2 | Transformer efficiency reported in User RMR equals Table 8.4.4 | pass | building/transformer/transformer/phase | value_equal_to | user | table | table_8.4.4 | transformer_efficiency

## Lookups
test_outcome_types | true/false | yes/no | applicable_rmr | rule_assertions | comparison_rmr
pass | true | Yes | User RMR | = | Expected Value
fail | false | No | Proposed RMR | <= | User RMR
manual_check |  |  | Baseline RMR | >= | Proposed RMR
caution |  |  |  |  | Baseline RMR